## Project Inputs
Electrical Distribution Design Package — Project Inputs | Column1 | Column2
Input | Value | Unit
Service voltage | 600 | V
Phase | 3 | phase
Customer load | 250 | kVA
Total route length | 85 | m
TX-01 to PB-01 | 45 | m
PB-01 to SE-01 | 40 | m
Duct bank configuration | 4 x 100 | mm PVC
Assumed duct bank depth | 0.9 | m
Existing grade elevation | 100 | m
Duct bank elevation | 99.1 | m

## Voltage Drop Calculation
Voltage Drop Calculation | Column1 | Column2
Parameter | Value | Unit
Load | 250 | kVA
Voltage | 600 | V
Calculated current | 240.5626 | A
Route length | 85 | m
Assumed conductor resistance | 0.000217 | ohm/m
Voltage drop | 7.6854 | V
Voltage drop percent | 1.2809 | %
Note: This is a simplified preliminary voltage drop check for academic portfolio use only.

## Cable Pull Review
Cable Pull Review | Column1 | Column2 | Column3 | Column4
Pull Segment | From | To | Length (m) | Review
Segment 1 | TX-01 | PB-01 | 45 | Acceptable
Segment 2 | PB-01 | SE-01 | 40 | Acceptable
Total Route | TX-01 | SE-01 | 85 | Split by pull box
Pull box PB-01 splits the 85 m route into two shorter pull segments.
This is a simplified cable pull review for academic portfolio use.
Final pulling tension and sidewall pressure require manufacturer data and detailed calculation.

## Quantity Takeoff
Quantity Takeoff | Column1 | Column2 | Column3
Item | Quantity | Unit | Basis
100 mm PVC duct | 340 | m | 4 ducts × 85 m
Secondary cable route | 85 | m | TX-01 to SE-01
Proposed pull box | 1 | ea | PB-01
Warning tape | 85 | m | Along trench route
Trench route | 85 | m | Total route length
Field verification points | 3 | ea | TX-01, PB-01, SE-01
Note: Quantities are preliminary and for academic portfolio use only.